## License Agreement
SunSpec Alliance
SunSpec Infomation Model Reference
Date Generated: 2021-12-09
This document is generated programatically from the canonical model definitions contained in the SunSpec model repository.
For the most up-to-date version of this document, go to: https://sunspec.org/sunspec-specifications/
Copyright SunSpec Alliance 2009-2021. All Rights Reserved.
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy. The complete policy of the SunSpec Alliance can be found at www.sunspec.org.
Prepared by the SunSpec Alliance
4040 Moorpark Avenue Suite 110
San Jose, CA 95117
Website: www.sunspec.org
Email: info@sunspec.org

## Summary
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter (superseded by the 700 series)
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | DER
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is programmatically generated from SunSpec model definition files, which can be downloaded from:
https://github.com/sunspec/models
Please note that the SunSpec model definition files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at:
https://sunspec.org/sunspec-specifications/
SunSpec Certification
If you would like to have your product SunSpec Certified you can apply for Certification here:
https://sunspec.org/sunspec-certification-application/
After applying, someone from SunSpec will followup shortly.
You can also contact certification@sunspec.org to ask questions and start the process.

## Index
Model | Label | Description
1 | Common | All SunSpec compliant devices must include this as the first model
211 | single phase (AN or AB) meter
212 | split single phase (ABN) meter
213 | wye-connect three phase (abcn) meter
214 | delta-connect three phase (abc) meter

## 1
Modbus address |  | Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
hex | dec |  |  | common |  |  | group | [6 empty] | Common | All SunSpec compliant devices must include this as the first model
9C42 | 40002 | 0 |  | ID | 1 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
9C43 | 40003 | 1 |  | L | 65 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
9C44 | 40004 | 2 |  | Mn |  |  | string | 16 |  |  |  | M | S | Manufacturer | Well known value registered with SunSpec for compliance
9C54 | 40020 | 18 |  | Md |  |  | string | 16 |  |  |  | M | S | Model | Manufacturer specific value (32 chars)
9C64 | 40036 | 34 |  | Opt |  |  | string | 8 |  |  |  |  | S | Options | Manufacturer specific value (16 chars)
9C6C | 40044 | 42 |  | Vr |  |  | string | 8 |  |  |  |  | S | Version | Manufacturer specific value (16 chars)
9C74 | 40052 | 50 |  | SN |  |  | string | 16 |  |  |  | M | S | Serial Number | Manufacturer specific value (32 chars)
9C84 | 40068 | 66 |  | DA |  |  | uint16 |  |  |  | RW |  |  | Device Address | Modbus device address
9C85 | 40069 | 67 |  | Pad |  |  | pad | [5 empty] | S |  | Force even alignment
Note on B3: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: Deve partire da 40002 e non da 40000 in quanto a 40000 devono essere inseriti i 2 valori 0x5375 e 0x6E53 (valore hex della stringa ASCII “SunS”). Vedi paragrafo 6.1.1 di SunSpec-Device-Information-Model-Specificiation-V1-1-final.pdf
Note on E4: L: A value that is the length of the device model in Modbus 16-bit registers. This value does NOT include the ID or L. I.e. it is the number of registers that follow the length. For the Common Model, this value is 66 but may be 65. All SunSpec models should be of even length. Common Models of length 66 shall contain the SunSpec pad16 value as the final register.
Note on F4: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: Deve essere pari a 65 o al massimo a 66 se si vuole pari, ma non a 64 in quanto non funziona.
Note on E11: Pad: SunSpec pad16 register. Must be included for Common Models of length 66. Not included if length is 65. In EMS NON gestiamo il DA (Device Address) quindi la lunghezza del modello è 65 e il Pad non serve. L'indirizzo per il modello successivo sarà quindi 40066 (0x9C82)

## 211
Modbus address |  | Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
hex | dec |  | 40069 | ac_meter |  |  | group | [6 empty] | single phase (AN or AB) meter
9C85 | 40069 | 0 |  | ID | 211 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
9C86 | 40070 | 1 |  | L | 124 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
9C87 | 40071 | 2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
9C89 | 40073 | 4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
9C8B | 40075 | 6 |  | AphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | A |  |  |  | Amps PhaseB | Phase B Current
9C8D | 40077 | 8 |  | AphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
9C8F | 40079 | 10 |  | PhV |  |  | float32 |  |  | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
9C91 | 40081 | 12 |  | PhVphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage AN | Phase Voltage AN
9C93 | 40083 | 14 |  | PhVphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN
9C95 | 40085 | 16 |  | PhVphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
9C97 | 40087 | 18 |  | PPV | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Voltage LL | Line to Line AC Voltage (average of active phases)
9C99 | 40089 | 20 |  | PPVphAB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
9C9B | 40091 | 22 |  | PPVphBC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
9C9D | 40093 | 24 |  | PPVphCA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
9C9F | 40095 | 26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
9CA1 | 40097 | 28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
9CA3 | 40099 | 30 |  | WphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | W |  |  |  | Watts phase A
9CA5 | 40101 | 32 |  | WphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | W |  |  |  | Watts phase B
9CA7 | 40103 | 34 |  | WphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | W |  |  |  | Watts phase C
9CA9 | 40105 | 36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
9CAB | 40107 | 38 |  | VAphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VA |  |  |  | VA phase A
9CAD | 40109 | 40 |  | VAphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VA |  |  |  | VA phase B
9CAF | 40111 | 42 |  | VAphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VA |  |  |  | VA phase C
9CB1 | 40113 | 44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
9CB3 | 40115 | 46 |  | VARphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | var |  |  |  | VAR phase A
9CB5 | 40117 | 48 |  | VARphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | var |  |  |  | VAR phase B
9CB7 | 40119 | 50 |  | VARphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | var |  |  |  | VAR phase C
9CB9 | 40121 | 52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
9CBB | 40123 | 54 |  | PFphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | PF |  |  |  | PF phase A
9CBD | 40125 | 56 |  | PFphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | PF |  |  |  | PF phase B
9CBF | 40127 | 58 |  | PFphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | PF |  |  |  | PF phase C
9CC1 | 40129 | 60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
9CC3 | 40131 | 62 |  | TotWhExpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
9CC5 | 40133 | 64 |  | TotWhExpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
9CC7 | 40135 | 66 |  | TotWhExpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
9CC9 | 40137 | 68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
9CCB | 40139 | 70 |  | TotWhImpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
9CCD | 40141 | 72 |  | TotWhImpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
9CCF | 40143 | 74 |  | TotWhImpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
9CD1 | 40145 | 76 |  | TotVAhExp | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
9CD3 | 40147 | 78 |  | TotVAhExpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
9CD5 | 40149 | 80 |  | TotVAhExpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
9CD7 | 40151 | 82 |  | TotVAhExpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
9CD9 | 40153 | 84 |  | TotVAhImp | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
9CDB | 40155 | 86 |  | TotVAhImpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
9CDD | 40157 | 88 |  | TotVAhImpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
9CDF | 40159 | 90 |  | TotVAhImpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
9CE1 | 40161 | 92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
9CE3 | 40163 | 94 |  | TotVArhImpQ1phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
9CE5 | 40165 | 96 |  | TotVArhImpQ1phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
9CE7 | 40167 | 98 |  | TotVArhImpQ1phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
9CE9 | 40169 | 100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
9CEB | 40171 | 102 |  | TotVArhImpQ2phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
9CED | 40173 | 104 |  | TotVArhImpQ2phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
9CEF | 40175 | 106 |  | TotVArhImpQ2phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
9CF1 | 40177 | 108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
9CF3 | 40179 | 110 |  | TotVArhExpQ3phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
9CF5 | 40181 | 112 |  | TotVArhExpQ3phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
9CF7 | 40183 | 114 |  | TotVArhExpQ3phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
9CF9 | 40185 | 116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
9CFB | 40187 | 118 |  | TotVArhExpQ4phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
9CFD | 40189 | 120 |  | TotVArhExpQ4phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
9CFF | 40191 | 122 |  | TotVArhExpQ4phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
9D01 | 40193 | 124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  |  |  | M_EVENT_Power_Failure | 2
|  |  |  | M_EVENT_Under_Voltage | 3
|  |  |  | M_EVENT_Low_PF | 4
|  |  |  | M_EVENT_Over_Current | 5
|  |  |  | M_EVENT_Over_Voltage | 6
|  |  |  | M_EVENT_Missing_Sensor | 7
|  |  |  | M_EVENT_Reserved1 | 8
|  |  |  | M_EVENT_Reserved2 | 9
|  |  |  | M_EVENT_Reserved3 | 10
|  |  |  | M_EVENT_Reserved4 | 11
|  |  |  | M_EVENT_Reserved5 | 12
|  |  |  | M_EVENT_Reserved6 | 13
|  |  |  | M_EVENT_Reserved7 | 14
|  |  |  | M_EVENT_Reserved8 | 15
|  |  |  | M_EVENT_OEM01 | 16
|  |  |  | M_EVENT_OEM02 | 17
|  |  |  | M_EVENT_OEM03 | 18
|  |  |  | M_EVENT_OEM04 | 19
|  |  |  | M_EVENT_OEM05 | 20
|  |  |  | M_EVENT_OEM06 | 21
|  |  |  | M_EVENT_OEM07 | 22
|  |  |  | M_EVENT_OEM08 | 23
|  |  |  | M_EVENT_OEM09 | 24
|  |  |  | M_EVENT_OEM10 | 25
|  |  |  | M_EVENT_OEM11 | 26
|  |  |  | M_EVENT_OEM12 | 27
|  |  |  | M_EVENT_OEM13 | 28
|  |  |  | M_EVENT_OEM14 | 29
|  |  |  | M_EVENT_OEM15 | 30
Note on F13: Alessandro Fardin: Nel caso di meter usato in connessione A-B , la tensione va letta L-N o A-N

## 212
Modbus address |  | Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
hex | dec |  | 40068 | ac_meter |  |  | group | [6 empty] | split single phase (ABN) meter
9C84 | 40068 | 0 |  | ID | 212 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
9C85 | 40069 | 1 |  | L | 124 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
9C86 | 40070 | 2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
9C88 | 40072 | 4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
9C8A | 40074 | 6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
9C8C | 40076 | 8 |  | AphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
9C8E | 40078 | 10 |  | PhV |  |  | float32 |  |  | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
9C90 | 40080 | 12 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
9C92 | 40082 | 14 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
9C94 | 40084 | 16 |  | PhVphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
9C96 | 40086 | 18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
9C98 | 40088 | 20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
9C9A | 40090 | 22 |  | PPVphBC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
9C9C | 40092 | 24 |  | PPVphCA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
9C9E | 40094 | 26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
9CA0 | 40096 | 28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
9CA2 | 40098 | 30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
9CA4 | 40100 | 32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
9CA6 | 40102 | 34 |  | WphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | W |  |  |  | Watts phase C
9CA8 | 40104 | 36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
9CAA | 40106 | 38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
9CAC | 40108 | 40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
9CAE | 40110 | 42 |  | VAphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VA |  |  |  | VA phase C
9CB0 | 40112 | 44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
9CB2 | 40114 | 46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
9CB4 | 40116 | 48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
9CB6 | 40118 | 50 |  | VARphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | var |  |  |  | VAR phase C
9CB8 | 40120 | 52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
9CBA | 40122 | 54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
9CBC | 40124 | 56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
9CBE | 40126 | 58 |  | PFphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | PF |  |  |  | PF phase C
9CC0 | 40128 | 60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
9CC2 | 40130 | 62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
9CC4 | 40132 | 64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
9CC6 | 40134 | 66 |  | TotWhExpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
9CC8 | 40136 | 68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
9CCA | 40138 | 70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
9CCC | 40140 | 72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
9CCE | 40142 | 74 |  | TotWhImpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
9CD0 | 40144 | 76 |  | TotVAhExp | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
9CD2 | 40146 | 78 |  | TotVAhExpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
9CD4 | 40148 | 80 |  | TotVAhExpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
9CD6 | 40150 | 82 |  | TotVAhExpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
9CD8 | 40152 | 84 |  | TotVAhImp | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
9CDA | 40154 | 86 |  | TotVAhImpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
9CDC | 40156 | 88 |  | TotVAhImpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
9CDE | 40158 | 90 |  | TotVAhImpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
9CE0 | 40160 | 92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
9CE2 | 40162 | 94 |  | TotVArhImpQ1phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
9CE4 | 40164 | 96 |  | TotVArhImpQ1phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
9CE6 | 40166 | 98 |  | TotVArhImpQ1phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
9CE8 | 40168 | 100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
9CEA | 40170 | 102 |  | TotVArhImpQ2phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
9CEC | 40172 | 104 |  | TotVArhImpQ2phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
9CEE | 40174 | 106 |  | TotVArhImpQ2phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
9CF0 | 40176 | 108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
9CF2 | 40178 | 110 |  | TotVArhExpQ3phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
9CF4 | 40180 | 112 |  | TotVArhExpQ3phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
9CF6 | 40182 | 114 |  | TotVArhExpQ3phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
9CF8 | 40184 | 116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
9CFA | 40186 | 118 |  | TotVArhExpQ4phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
9CFC | 40188 | 120 |  | TotVArhExpQ4phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
9CFE | 40190 | 122 |  | TotVArhExpQ4phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
9D00 | 40192 | 124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  |  |  | M_EVENT_Power_Failure | 2
|  |  |  | M_EVENT_Under_Voltage | 3
|  |  |  | M_EVENT_Low_PF | 4
|  |  |  | M_EVENT_Over_Current | 5
|  |  |  | M_EVENT_Over_Voltage | 6
|  |  |  | M_EVENT_Missing_Sensor | 7
|  |  |  | M_EVENT_Reserved1 | 8
|  |  |  | M_EVENT_Reserved2 | 9
|  |  |  | M_EVENT_Reserved3 | 10
|  |  |  | M_EVENT_Reserved4 | 11
|  |  |  | M_EVENT_Reserved5 | 12
|  |  |  | M_EVENT_Reserved6 | 13
|  |  |  | M_EVENT_Reserved7 | 14
|  |  |  | M_EVENT_Reserved8 | 15
|  |  |  | M_EVENT_OEM01 | 16
|  |  |  | M_EVENT_OEM02 | 17
|  |  |  | M_EVENT_OEM03 | 18
|  |  |  | M_EVENT_OEM04 | 19
|  |  |  | M_EVENT_OEM05 | 20
|  |  |  | M_EVENT_OEM06 | 21
|  |  |  | M_EVENT_OEM07 | 22
|  |  |  | M_EVENT_OEM08 | 23
|  |  |  | M_EVENT_OEM09 | 24
|  |  |  | M_EVENT_OEM10 | 25
|  |  |  | M_EVENT_OEM11 | 26
|  |  |  | M_EVENT_OEM12 | 27
|  |  |  | M_EVENT_OEM13 | 28
|  |  |  | M_EVENT_OEM14 | 29
|  |  |  | M_EVENT_OEM15 | 30

## 213
Modbus address |  | Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
hex | dec |  | 40068 | ac_meter |  |  | group | [6 empty] | wye-connect three phase (abcn) meter
9C84 | 40068 | 0 |  | ID | 213 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
9C85 | 40069 | 1 |  | L | 124 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
9C86 | 40070 | 2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current (nota: I1+I2+I3)
9C88 | 40072 | 4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
9C8A | 40074 | 6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
9C8C | 40076 | 8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current
9C8E | 40078 | 10 |  | PhV |  |  | float32 |  |  | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
9C90 | 40080 | 12 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
9C92 | 40082 | 14 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
9C94 | 40084 | 16 |  | PhVphC |  |  | float32 |  |  | V |  | M |  | Phase Voltage CN | Phase Voltage CN
9C96 | 40086 | 18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
9C98 | 40088 | 20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
9C9A | 40090 | 22 |  | PPVphBC |  |  | float32 |  |  | V |  | M |  | Phase Voltage BC | Phase Voltage BC
9C9C | 40092 | 24 |  | PPVphCA |  |  | float32 |  |  | V |  | M |  | Phase Voltage CA | Phase Voltage CA
9C9E | 40094 | 26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
9CA0 | 40096 | 28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
9CA2 | 40098 | 30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
9CA4 | 40100 | 32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
9CA6 | 40102 | 34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
9CA8 | 40104 | 36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
9CAA | 40106 | 38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
9CAC | 40108 | 40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
9CAE | 40110 | 42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
9CB0 | 40112 | 44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
9CB2 | 40114 | 46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
9CB4 | 40116 | 48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
9CB6 | 40118 | 50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
9CB8 | 40120 | 52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
9CBA | 40122 | 54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
9CBC | 40124 | 56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
9CBE | 40126 | 58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
9CC0 | 40128 | 60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
9CC2 | 40130 | 62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
9CC4 | 40132 | 64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
9CC6 | 40134 | 66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
9CC8 | 40136 | 68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
9CCA | 40138 | 70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
9CCC | 40140 | 72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
9CCE | 40142 | 74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
9CD0 | 40144 | 76 |  | TotVAhExp | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
9CD2 | 40146 | 78 |  | TotVAhExpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
9CD4 | 40148 | 80 |  | TotVAhExpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
9CD6 | 40150 | 82 |  | TotVAhExpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
9CD8 | 40152 | 84 |  | TotVAhImp | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
9CDA | 40154 | 86 |  | TotVAhImpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
9CDC | 40156 | 88 |  | TotVAhImpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
9CDE | 40158 | 90 |  | TotVAhImpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
9CE0 | 40160 | 92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
9CE2 | 40162 | 94 |  | TotVArhImpQ1phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
9CE4 | 40164 | 96 |  | TotVArhImpQ1phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
9CE6 | 40166 | 98 |  | TotVArhImpQ1phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
9CE8 | 40168 | 100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
9CEA | 40170 | 102 |  | TotVArhImpQ2phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
9CEC | 40172 | 104 |  | TotVArhImpQ2phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
9CEE | 40174 | 106 |  | TotVArhImpQ2phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
9CF0 | 40176 | 108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
9CF2 | 40178 | 110 |  | TotVArhExpQ3phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
9CF4 | 40180 | 112 |  | TotVArhExpQ3phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
9CF6 | 40182 | 114 |  | TotVArhExpQ3phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
9CF8 | 40184 | 116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
9CFA | 40186 | 118 |  | TotVArhExpQ4phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
9CFC | 40188 | 120 |  | TotVArhExpQ4phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
9CFE | 40190 | 122 |  | TotVArhExpQ4phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
9D00 | 40192 | 124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  |  |  | M_EVENT_Power_Failure | 2
|  |  |  | M_EVENT_Under_Voltage | 3
|  |  |  | M_EVENT_Low_PF | 4
|  |  |  | M_EVENT_Over_Current | 5
|  |  |  | M_EVENT_Over_Voltage | 6
|  |  |  | M_EVENT_Missing_Sensor | 7
|  |  |  | M_EVENT_Reserved1 | 8
|  |  |  | M_EVENT_Reserved2 | 9
|  |  |  | M_EVENT_Reserved3 | 10
|  |  |  | M_EVENT_Reserved4 | 11
|  |  |  | M_EVENT_Reserved5 | 12
|  |  |  | M_EVENT_Reserved6 | 13
|  |  |  | M_EVENT_Reserved7 | 14
|  |  |  | M_EVENT_Reserved8 | 15
|  |  |  | M_EVENT_OEM01 | 16
|  |  |  | M_EVENT_OEM02 | 17
|  |  |  | M_EVENT_OEM03 | 18
|  |  |  | M_EVENT_OEM04 | 19
|  |  |  | M_EVENT_OEM05 | 20
|  |  |  | M_EVENT_OEM06 | 21
|  |  |  | M_EVENT_OEM07 | 22
|  |  |  | M_EVENT_OEM08 | 23
|  |  |  | M_EVENT_OEM09 | 24
|  |  |  | M_EVENT_OEM10 | 25
|  |  |  | M_EVENT_OEM11 | 26
|  |  |  | M_EVENT_OEM12 | 27
|  |  |  | M_EVENT_OEM13 | 28
|  |  |  | M_EVENT_OEM14 | 29
|  |  |  | M_EVENT_OEM15 | 30

## 214
Modbus address |  | Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
hex | dec |  | 40068 | ac_meter |  |  | group | [6 empty] | delta-connect three phase (abc) meter
9C84 | 40068 | 0 |  | ID | 214 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
9C85 | 40069 | 1 |  | L | 124 |  | uint16 |  |  |  |  | M | S | Model Length | Model length
9C86 | 40070 | 2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current (nota: I1+I2+I3)
9C88 | 40072 | 4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
9C8A | 40074 | 6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
9C8C | 40076 | 8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current
9C8E | 40078 | 10 |  | PhV | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
9C90 | 40080 | 12 |  | PhVphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage AN | Phase Voltage AN
9C92 | 40082 | 14 |  | PhVphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN
9C94 | 40084 | 16 |  | PhVphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
9C96 | 40086 | 18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
9C98 | 40088 | 20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
9C9A | 40090 | 22 |  | PPVphBC |  |  | float32 |  |  | V |  | M |  | Phase Voltage BC | Phase Voltage BC
9C9C | 40092 | 24 |  | PPVphCA |  |  | float32 |  |  | V |  | M |  | Phase Voltage CA | Phase Voltage CA
9C9E | 40094 | 26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
9CA0 | 40096 | 28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
9CA2 | 40098 | 30 |  | WphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | W |  |  |  | Watts phase A
9CA4 | 40100 | 32 |  | WphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | W |  |  |  | Watts phase B
9CA6 | 40102 | 34 |  | WphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | W |  |  |  | Watts phase C
9CA8 | 40104 | 36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
9CAA | 40106 | 38 |  | VAphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VA |  |  |  | VA phase A
9CAC | 40108 | 40 |  | VAphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VA |  |  |  | VA phase B
9CAE | 40110 | 42 |  | VAphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VA |  |  |  | VA phase C
9CB0 | 40112 | 44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
9CB2 | 40114 | 46 |  | VARphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | var |  |  |  | VAR phase A
9CB4 | 40116 | 48 |  | VARphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | var |  |  |  | VAR phase B
9CB6 | 40118 | 50 |  | VARphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | var |  |  |  | VAR phase C
9CB8 | 40120 | 52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
9CBA | 40122 | 54 |  | PFphA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | PF |  |  |  | PF phase A
9CBC | 40124 | 56 |  | PFphB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | PF |  |  |  | PF phase B
9CBE | 40126 | 58 |  | PFphC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | PF |  |  |  | PF phase C
9CC0 | 40128 | 60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
9CC2 | 40130 | 62 |  | TotWhExpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
9CC4 | 40132 | 64 |  | TotWhExpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
9CC6 | 40134 | 66 |  | TotWhExpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
9CC8 | 40136 | 68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
9CCA | 40138 | 70 |  | TotWhImpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
9CCC | 40140 | 72 |  | TotWhImpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
9CCE | 40142 | 74 |  | TotWhImpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
9CD0 | 40144 | 76 |  | TotVAhExp | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
9CD2 | 40146 | 78 |  | TotVAhExpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
9CD4 | 40148 | 80 |  | TotVAhExpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
9CD6 | 40150 | 82 |  | TotVAhExpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
9CD8 | 40152 | 84 |  | TotVAhImp | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
9CDA | 40154 | 86 |  | TotVAhImpPhA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
9CDC | 40156 | 88 |  | TotVAhImpPhB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
9CDE | 40158 | 90 |  | TotVAhImpPhC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
9CE0 | 40160 | 92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
9CE2 | 40162 | 94 |  | TotVArhImpQ1phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
9CE4 | 40164 | 96 |  | TotVArhImpQ1phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
9CE6 | 40166 | 98 |  | TotVArhImpQ1phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
9CE8 | 40168 | 100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
9CEA | 40170 | 102 |  | TotVArhImpQ2phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
9CEC | 40172 | 104 |  | TotVArhImpQ2phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
9CEE | 40174 | 106 |  | TotVArhImpQ2phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
9CF0 | 40176 | 108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
9CF2 | 40178 | 110 |  | TotVArhExpQ3phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
9CF4 | 40180 | 112 |  | TotVArhExpQ3phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
9CF6 | 40182 | 114 |  | TotVArhExpQ3phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
9CF8 | 40184 | 116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
9CFA | 40186 | 118 |  | TotVArhExpQ4phA | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
9CFC | 40188 | 120 |  | TotVArhExpQ4phB | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
9CFE | 40190 | 122 |  | TotVArhExpQ4phC | Not Implemented: 0x7FC00000 (NaN) |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
9D00 | 40192 | 124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  |  |  | M_EVENT_Power_Failure | 2
|  |  |  | M_EVENT_Under_Voltage | 3
|  |  |  | M_EVENT_Low_PF | 4
|  |  |  | M_EVENT_Over_Current | 5
|  |  |  | M_EVENT_Over_Voltage | 6
|  |  |  | M_EVENT_Missing_Sensor | 7
|  |  |  | M_EVENT_Reserved1 | 8
|  |  |  | M_EVENT_Reserved2 | 9
|  |  |  | M_EVENT_Reserved3 | 10
|  |  |  | M_EVENT_Reserved4 | 11
|  |  |  | M_EVENT_Reserved5 | 12
|  |  |  | M_EVENT_Reserved6 | 13
|  |  |  | M_EVENT_Reserved7 | 14
|  |  |  | M_EVENT_Reserved8 | 15
|  |  |  | M_EVENT_OEM01 | 16
|  |  |  | M_EVENT_OEM02 | 17
|  |  |  | M_EVENT_OEM03 | 18
|  |  |  | M_EVENT_OEM04 | 19
|  |  |  | M_EVENT_OEM05 | 20
|  |  |  | M_EVENT_OEM06 | 21
|  |  |  | M_EVENT_OEM07 | 22
|  |  |  | M_EVENT_OEM08 | 23
|  |  |  | M_EVENT_OEM09 | 24
|  |  |  | M_EVENT_OEM10 | 25
|  |  |  | M_EVENT_OEM11 | 26
|  |  |  | M_EVENT_OEM12 | 27
|  |  |  | M_EVENT_OEM13 | 28
|  |  |  | M_EVENT_OEM14 | 29
|  |  |  | M_EVENT_OEM15 | 30